## HR-Systems
HR-System according DIN EN 308 |  |  |  |  | The term per year can be selected variably
Temp. Efficiency | % | 70 | 70 | 70 | 70
Capacity | kW | 218.645 | 218.645 | 218.645 | 218.645
Therm per year | Hours | 2080 | 2080 | 2080 | 2080
Electricity price | EUR/MWh | 100 | 100 | 100 | 100
Air flow per HE | m3/h | 50000 | 50000 | 50000 | 50000 | Zeller Consulting Suisse
Pressure drop per HE | Pa | 112.1985 | 121.53 | 130.407 | 138.939 | HVAC Solutions
Efficiency | --- | 0.7 | 0.7 | 0.7 | 0.7 | Jurastrasse 35
2 Fans | kW | 4.4523 | 4.8226 | 5.1749 | 5.5135 | CH-3063 Ittigen
2 Fans | MWh | 9.2608 | 10.031 | 10.7638 | 11.468 | info@zcs.ch
2 Fans | EUR | 926.0829 | 1003.1048 | 1076.3752 | 1146.7981 | www.zcs.ch
Intermediate medium | m3/h | 14.705 | 14.684 | 14.663 | 14.652
Pressure drop per HE | kPa | 218.1485 | 80.808 | 47.2925 | 33.4475
Efficiency | --- | 0.8 | 0.8 | 0.8 | 0.8
1 Pump | kW | 2.2277 | 0.82402 | 0.48156 | 0.34033
1 Pump | MWh | 4.6336 | 1.714 | 1.0016 | 0.70788
1 Pump | EUR | 463.3595 | 171.3956 | 100.165 | 70.7883
Maintenance costs | EUR | 3241.9107 | 3602.313 | 3951.7682 | 4292.3287 | 5% of the investment costs
Operating costs | EUR | 4631.353 | 4776.8133 | 5128.3084 | 5509.9151 | Total operating costs
Installation depth | mm | 2 x 600 | 2 x 670 | 2 x 740 | 2 x 810
Tube rows | Piece | 2 x 14 | 2 x 16 | 2 x 18 | 2 x 20
Two-part HE | EUR | 41696.6 | 46332 | 50826.6 | 55206.8 | With 20% surcharge for two-piece HE
Air conditioning unit | EUR | 2084.83 | 2316.6 | 2541.33 | 2760.34 | Proportional costs
2 Fans | EUR | 208.483 | 231.66 | 254.133 | 276.034 | Proportional costs
Hydr. & controllers | EUR | 20848.3 | 23166 | 25413.3 | 27603.4
Investment costs | EUR | 64838.213 | 72046.26 | 79035.363 | 85846.574 | Total investment costs
Inv.costs per year | EUR | 4322.5475 | 4803.084 | 5269.0242 | 5723.1049 | Amortization in 15 years
Amortization | EUR | 8953.9006 | 9579.8973 | 10397.3326 | 11233.02 | Amortization costs per year
Costs per year (EUR)
|  |  |  | Bern | 540 meter over sea level (950 hPa)
|  |  |  | Outside air | 50'000m3/h, 5°C/0%
2 m/s flow velocity
|  |  |  | Return air | 50'000m3/h, 25°C/0%
2 m/s flow velocity
|  |  |  | Operation | 52 weeks
[5 empty] | 5 days a week |  | 2080 hours per year
8 hours per day
Amortization costs
Operation costs
Electriciy costs for 2 fans
Electricity costs for 1 pump
Lower the operating time per year, more sensible it is to have high pressure drops on the intermediate medium due to the high fixed costs. Furthermore, the intermediate carrier pressure drops should be high for the nominal air volume in order not to fall into the laminar range in partial load operation. 25% ethylene glycol was used as the intermediate medium, although Temper-20 would be more sensible.
We recommend intermediate medium pressure drops of 200 kPa per heat exchanger, which has a positive effect on the temperature efficiency andcapacity. With moderately corrugated fins from Walter Roller, very small air-side pressure drops result. Nevertheless, the additional energy costs due to the heat recovery system for the two fans are significantly higher than for the pump. From this, it can be concluded that the much smaller intermediate medium pressure drops often required make no sense. In fact, the air-side heat exchanger pressure drops are a problem if fins with too strong a profile are used.
Intermediate medium pressure drop per HE (kPa)